## Misc IO
MISCELLANEOUS CONTROL AND MONITORING INDEX | [9 empty] | C.0.0
DESCRIPTION |  | CONTROLLABLE ITEMS | MONITORED ITEMS | ADB PROVIDED CONTROL OR MONITORING DESCRIPTION | ACE™ NUMBER |  | ACE™ I/O CONNECTION | COMMENTS / MISCELLANEOUS NOTES | Comm Ch 1 | Comm Ch 2
1023 - Generator Running |  | YES | YES (CSR) | (1) DRY CONTACT ENCLOSURE ; 250VAC ; MAX 1A
1
0
CCR Index & Miscellaneuos I/O Approval
| Print Name |  |  |  |  | Date
Approved by
Representing

## CCR Index
CCR INDEX | [21 empty] | C.0.0
CCR # | ACE # | Control Configuration | COM Ch 1 | COM Ch 2 | CCR Name Line 1 | CCR Name Line 2 | kW | Internal CCI Voltage | Output Current | Lamps Out | Manufacturer and Model | Input Monitoring | Output Monitoring | BRITE Master # | Remote Count | ACE Integrated | Circuit Selector Name | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Input Voltage | 6
1 | 1 | 5-STEP 1-LOOP |  |  | RWY EDGE |  | 20 | 120VAC | 6.6 | NO | HONEYWELL | NONE | NONE
2 | 2 | 3-STEP 1-LOOP |  |  | TWY EDGE |  | 7.5 | 120VAC | 6.6 | NO | ADB SIGNATURE FERRO | NONE | NONE

## Circuit Definition
Presets, Touchscreen Pages, & Circuit Definitions
Preset Definitions |  |  | Touchscreen Pages |  |  |  | C.0.0
ID | Description |  | ID | Description
1 | 18 |  | 1 | Preset
2 | 36 |  | 2 | Runway
3 |  |  | 3 | Taxiway
4 |  |  | 4
5 |  |  | 5
6 |  |  | 6
7 |  |  | 7
8 |  |  | 8
9 |  |  | 9
10 |  |  | 10
11 |  |  | 11
12 |  |  | 12
13 |  |  | 13
14 |  |  | 14
15 |  |  | 15
Circuit Definitions
ID | Button Descriptions | Page | Type | Steps | Elements
1 | Runway 18 | Runway | Runway | 5 | RWY EDGE
2 | Taxiway A Edge | Taxiway | Taxiway | 3 | TWY EDGE
Presets, Pages, & Circuit Definition Approval
Print Name
Date
Approved by
Representing

## Control Methodology
Visibility |  | Day | [15 empty] | Night
Greater Than 5 Miles |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 0 | 0 | [14 empty] | 1 | 1
2 | Taxiway A Edge | 0 | 0 | [14 empty] | 1 | 1
Greater Than 5 Miles Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Visibility |  | Day | [15 empty] | Night
3 To 5 Miles |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 0 | 0 | [14 empty] | 2 | 2
2 | Taxiway A Edge | 0 | 0 | [14 empty] | 1 | 1
3 To 5 Miles Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Visibility |  | Day | [15 empty] | Night
2 To 3 Miles |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 3 | 3 | [14 empty] | 3 | 3
2 | Taxiway A Edge | 0 | 0 | [14 empty] | 1 | 1
2 To 3 Miles Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Visibility |  | Day | [15 empty] | Night
1 To 2 Miles |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 4 | 4 | [14 empty] | 3 | 3
2 | Taxiway A Edge | 0 | 0 | [14 empty] | 1 | 1
1 To 2 Miles Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Visibility |  | Day | [15 empty] | Night
Less Than 1 Mile |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 5 | 5 | [14 empty] | 4 | 4
2 | Taxiway A Edge | 3 | 3 | [14 empty] | 2 | 2
Less Than 1 Mile Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Visibility |  | Day | [15 empty] | Night
Less Than 1200 Feet |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 18 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ID | Button Descriptions
1 | Runway 18 | 5 | 5 | [14 empty] | 4 | 4
2 | Taxiway A Edge | 3 | 3 | [14 empty] | 2 | 2
Less Than 1200 Feet Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0
Special |  | Radio 1 | [8 empty] | Radio 2 | [8 empty] | Radio 3
Radio Control |  | Default |  | Low (3 Clicks) |  | Medium (5 Clicks) |  | High (7 Clicks) |  |  | Default |  | Low (3 Clicks) |  | Medium (5 Clicks) |  | High (7 Clicks) |  |  | Default |  | Low (3 Clicks) |  | Medium (5 Clicks) |  | High (7 Clicks)
ID | Button Descriptions
1 | Runway 18
2 | Taxiway A Edge
Radio Control Approval
| Approved by | [19 empty] | Date
Print Name
Representing
C.0.0

## FAAO 7110.65R
| Generic Visibility Table (150-5345-56) | [7 empty] | Sequence Flashing Lights (SFL)
| Range | Day |  |  | Night |  |  |  | Range | Day |  |  | Night
|  | 5 | 3 | 1 | 5 | 3 | 1 |  |  |  | 3 | 1 |  | 3 | 1
1 | Less Than 1200 Feet | 5 | 3 | 1 | 5 | 3 | 1 | 1 | Less Than 1200 Feet |  | 3 | 1 |  | 2 | 1
2 | Less Than 1 Mile | 5 | 3 | 0 | 4 | 2 | 1 | 2 | Less Than 1 Mile |  | 3 | 1 |  | 2 | 1
3 | 1 To 2 Miles | 4 | 0 | 0 | 3 | 1 | 1 | 3 | 1 To 2 Miles |  | 2 | 1 |  | 2 | 1
4 | 2 To 3 Miles | 3 | 0 | 0 | 3 | 1 | 1 | 4 | 2 To 3 Miles |  | 2 | 1 |  | 2 | 1
5 | 3 To 5 Miles | 0 | 0 | 0 | 2 | 1 | 1 | 5 | 3 To 5 Miles |  | 1 | 1 |  | 1 | 1
6 | Greater Than 5 Miles | 0 | 0 | 0 | 1 | 1 | 1 | 6 | Greater Than 5 Miles |  | 1 | 1 |  | 1 | 1
| Runway End Identifier Lights (REIL) | [7 empty] | Runways, Runway Centerline Lights, & Touchdown Zones
| Range | Day |  |  | Night |  |  |  | Range | Day |  |  | Night
|  |  | 3 |  |  | 3 |  |  |  | 5 | 3 |  | 5 | 3
1 | Less Than 1200 Feet |  | 3 |  |  | 3 |  | 1 | Less Than 1200 Feet | 5 | 3 |  | 4 | 3
2 | Less Than 1 Mile |  | 3 |  |  | 3 |  | 2 | Less Than 1 Mile | 5 | 3 |  | 4 | 3
3 | 1 To 2 Miles |  | 3 |  |  | 2 |  | 3 | 1 To 2 Miles | 4 | 3 |  | 3 | 2
4 | 2 To 3 Miles |  | 2 |  |  | 2 |  | 4 | 2 To 3 Miles | 3 | 2 |  | 3 | 2
5 | 3 To 5 Miles |  | 2 |  |  | 1 |  | 5 | 3 To 5 Miles | 0 | 0 |  | 2 | 1
6 | Greater Than 5 Miles |  | 0 |  |  | 1 |  | 6 | Greater Than 5 Miles | 0 | 0 |  | 1 | 1
| Visual Approach Slope Indicators (VASI) | [7 empty] | Taxiways, Taxiway Centerline Lights
| Range | Day |  |  | Night |  |  |  | Range | Day |  |  | Night
|  |  | 3 | 2 |  | 3 | 2 |  |  | 5 | 3 | 1 | 5 | 3 | 1
1 | Less Than 1200 Feet |  | 3 | 2 |  | 1 | 1 | 1 | Less Than 1200 Feet | 5 | 3 | 1 | 4 | 2 | 1
2 | Less Than 1 Mile |  | 3 | 2 |  | 1 | 1 | 2 | Less Than 1 Mile | 5 | 3 | 1 | 4 | 2 | 1
3 | 1 To 2 Miles |  | 3 | 2 |  | 1 | 1 | 3 | 1 To 2 Miles | 0 | 0 | 0 | 3 | 1 | 1
4 | 2 To 3 Miles |  | 3 | 2 |  | 1 | 1 | 4 | 2 To 3 Miles | 0 | 0 | 0 | 3 | 1 | 1
5 | 3 To 5 Miles |  | 3 | 2 |  | 1 | 1 | 5 | 3 To 5 Miles | 0 | 0 | 0 | 2 | 1 | 1
6 | Greater Than 5 Miles |  | 3 | 2 |  | 1 | 1 | 6 | Greater Than 5 Miles | 0 | 0 | 0 | 1 | 1 | 1
| Precision Approach Path Indicators (PAPI) | [7 empty] | Beacon
| Range | Day |  |  | Night |  |  |  | Range | Day |  |  | Night
|  | 5 |  |  | 5 | [6 empty] | 1 |  |  | 1
1 | Less Than 1200 Feet | 4 |  |  | 3 |  |  | 1 | Less Than 1200 Feet |  |  | 1 |  |  | 1
2 | Less Than 1 Mile | 4 |  |  | 3 |  |  | 2 | Less Than 1 Mile |  |  | 1 |  |  | 1
3 | 1 To 2 Miles | 4 |  |  | 3 |  |  | 3 | 1 To 2 Miles |  |  | 1 |  |  | 1
4 | 2 To 3 Miles | 4 |  |  | 3 |  |  | 4 | 2 To 3 Miles |  |  | 1 |  |  | 1
5 | 3 To 5 Miles | 4 |  |  | 3 |  |  | 5 | 3 To 5 Miles |  |  | 0 |  |  | 1
6 | Greater Than 5 Miles | 4 |  |  | 3 |  |  | 6 | Greater Than 5 Miles |  |  | 0 |  |  | 1
| Approach Lights (ALS) | [7 empty] | Medium Intensity Or Omnidirectional (MALSR/ODALS)
| Range | Day |  |  | Night |  |  |  | Range | Day |  |  | Night
|  | 5 |  |  | 5 | [5 empty] | 3 |  |  | 3
1 | Less Than 1200 Feet | 5 |  |  | 3 |  |  | 1 | Less Than 1200 Feet |  | 3 |  |  | 3
2 | Less Than 1 Mile | 5 |  |  | 3 |  |  | 2 | Less Than 1 Mile |  | 3 |  |  | 2
3 | 1 To 2 Miles | 4 |  |  | 3 |  |  | 3 | 1 To 2 Miles |  | 3 |  |  | 2
4 | 2 To 3 Miles | 4 |  |  | 3 |  |  | 4 | 2 To 3 Miles |  | 2 |  |  | 2
5 | 3 To 5 Miles | 3 |  |  | 1 |  |  | 5 | 3 To 5 Miles |  | 2 |  |  | 1
6 | Greater Than 5 Miles | 2 |  |  | 1 |  |  | 6 | Greater Than 5 Miles |  | 0 |  |  | 1

## Logs (hidden)
User | Workbook FullName | Sheet Name | Date | Time | Range | Old Value | New Value | Module | Event
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:11 | $A$4
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | ThisWorkbook | 2007-08-27 | 14:11 |  |  |  | Workbook_SheetChange | Error: [9] Subscript out of range
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $C$4 |  | 5-STEP 1-LOOP
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $A$4 |  | 1899-12-31
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $B$4 |  | 1
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $F$4 |  | RWY EDGE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $H$4 |  | 20
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $I$4 |  | 120VAC
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $J$4 |  | 6.6
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $K$4 |  | NO
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $L$4 | Manufacturer and Model | HONEYWELL
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $M$4 |  | NONE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:12 | $N$4 |  | CVM/IRMS
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 | $B$5 |  | 1900-01-17
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 | $B$6 |  | 36
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 | $E$5 |  | Preset
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 | $E$6 |  | Runway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 | $E$7 |  | Taxiway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:13 |  |  |  | BuildElements_Click | User clicked Build
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $A$5 |  | 2
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $C$5 |  | 3-STEP 1-LOOP
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $A$5 |  | 2
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $B$5 |  | 2
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $F$5 |  | TWY EDGE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $H$5 |  | 7.5
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $I$5 |  | 120VAC
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $J$5 |  | 6.6
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:13 | $K$5 |  | NO
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:14 | $L$5 |  | SIEMENS SIGNATURE FERRO
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:14 | $M$5 |  | NONE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:14 | $N$5 |  | NONE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | CCR Index | 2007-08-27 | 14:14 | $N$4 | CVM/IRMS | NONE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:14 |  |  |  | BuildElements_Click | User clicked Build
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:14 | $B$23 |  | Runway 18
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:14 | $B$24 |  | Taxiway A Edge
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:14 | $C$23 |  | Runway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:14 | $C$24 |  | Taxiway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $D$23 |  | Runway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $D$24 |  | Taxiway
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $E$23 |  | 5
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $E$24 |  | 3
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $F$23 |  | RWY EDGE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Circuit Definition | 2007-08-27 | 14:15 | $F$24 |  | TWY EDGE
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Control Methodology | 2007-08-27 | 14:15 |  |  |  | GoFAATables_Click | User clicked Use FAA Tables
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:19 | $A$3 |  | 1007 - New power reading
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:19 | $A$3
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:20 | $D$3 |  | YES
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:20 | $G$3 |  | YES (CSR)
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:20 | $J$3 |  | (1) DRY CONTACT ENCLOSURE ; 250VAC ; MAX 1A
stutcc | http://sascmhfsr01.sascmh.siemens.com/pdmweb/pdmwcgi.exe?Request=GetDoc&Document=Q0633.xls&Revision=&ZDoc=/Q0633.xls | Misc IO | 2007-08-27 | 14:21 | $A$3 |  | 1021 - Hydro power status
stutcc | P:\Project Engineering\8 - Project Engineering Reference Material\PEG - Sales Support\Engineering Seminar Presentations\Application Guide and Bid Specifications\ALCS Specification\Q0633 CCR Index.xls | Misc IO | 2007-09-10 | 11:51 | $A$3
stutcc | P:\Project Engineering\8 - Project Engineering Reference Material\PEG - Sales Support\Engineering Seminar Presentations\Application Guide and Bid Specifications\ALCS Specification\Q0633 CCR Index.xls | ThisWorkbook | 2007-09-10 | 11:51 |  |  |  | Workbook_SheetChange | Error: [9] Subscript out of range
stutcc | P:\Project Engineering\8 - Project Engineering Reference Material\PEG - Sales Support\Engineering Seminar Presentations\Application Guide and Bid Specifications\ALCS Specification\Q0633 CCR Index.xls | Circuit Definition | 2007-09-10 | 11:52 |  |  |  | BuildElements_Click | User clicked Build
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | CCR Index | 2010-03-15 | 17:00 | $L$5 | SIEMENS SIGNATURE FERRO | ADB SIGNATURE FERRO
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:08 | $G$15 | SIEMENS (ADB) OIL-FILLED | ADB (SIEMENS) OIL-FILLED
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:08 | $G$16 | SIEMENS (ADB) LC | SIEMENS (SIEMENS) LC
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:09 | $G$17 | SIEMENS (ADB) FERRO | SIEMENS (SIEMENS) FERRO
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:09 | $G$18 | SIEMENS SIGNATURE FERRO | ADB SIGNATURE FERRO
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:09 | $G$16 | SIEMENS (SIEMENS) LC | ADB (SIEMENS) LC
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:09 | $G$17 | SIEMENS (SIEMENS) FERRO | ADB (SIEMENS) FERRO
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:10 | $G$19 | WESTINGHOUSE
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:10 | $G$20 |  | UNKNOWN (GENERIC)
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:10 | $G$20 | WESTINGHOUSE | UNKNOWN (GENERIC)
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:10 | $G$21 |  | WESTINGHOUSE
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:11 | $G$19 |  | ADB SIGNATURE THYRISTOR
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:12 | $G$19
John Chapman | C:\Documents and Settings\jchapman\My Documents\Products\ALCMS\Q0633 CCR Index.xls | Lists | 2010-03-16 | 8:13 | $G$19 | ADB SIGNATURE THYRISTOR | ADB SIGNATURE THYRISTOR
mknox | L:\External Communication\Internet\_2011 Changes\John PC Updates\ALCMS PLC update\Q0633 CCR Index.xls | Misc IO | 2011-04-29 | 9:15 | $J$2 | SAS PROVIDED CONTROL OR MONITORING DESCRIPTION | ADB PROVIDED CONTROL OR MONITORING DESCRIPTION

## Lists (hidden)
3-STEP 1-LOOP | 1.5 | 6.6 | CROUSE-HINDS 31000 | INT | NONE | YES | 1001 - Clock set | YES | YES | (1) OPTO-ISOLATED ; DIGITAL INPUT ; 120VAC / 24VDC | None | 208 V | Input Channel 0 - J13 7, 8 | CCR Index | Enable Logging | TRUE | RWY EDGE | CCR Index | Generic | B5:H10 | C4:E4
3-STEP 2-LOOP | 4 | 20 | CROUSE-HINDS 36000 | EXT | CSR ONLY | NO | 1005 - Device now in step | NO | YES (CSR) | (1) DRY CONTACT ENCLOSURE ; 250VAC ; MAX 1A | 120VAC | 220 V | Input Channel 1 - J13 5, 6 | Misc IO | Log Sheet | Logs | TWY EDGE | Misc IO | Runway | K15:Q20 | L14:N14
3-STEP 3-LOOP | 7.5 |  | CROUSE-HINDS TYPE 2 | NONE | CSR/IRMS |  | 1006 - New voltage reading | ON / OFF | NO |  | 48VDC | 240 V | Input Channel 2 - J13 3, 4 | Circuit Definition | Version | C.0.0 | 1023 - Generator Running | Circuit Definition | Taxiway | K25:Q30 | L24:N24
3-STEP 4-LOOP | 10 |  | GE |  | CVM ONLY |  | 1007 - New power reading |  | ON / OFF |  | 24VDC | 347 V | Input Channel 3 - J13 1, 2 | Control Methodology |  |  |  | Control Methodology | REIL | B15:H20 | C14:E14
3-STEP SPARE | 15 |  | GENERAL SIGNAL |  | CVM/IRMS |  | 1008 - New current reading |  | 3-CLICK |  |  | 480 V |  | System Readiness Check |  |  |  | FAAO 7110.65R | VASI | B25:H30 | C24:E24
3-STEP CONTROL ONLY | 20 |  | HEVI-DUTY |  | IRMS ONLY |  | 1009 - New lamps out reading |  | 5-CLICK |  |  | 2400 V | Input Channel 4 - J14 7, 8 | CCR Import |  |  |  |  | PAPI | B35:H40 | C34:E34
3-STEP COMBO BOX | 30 |  | HEVI-DUTY TYPE 2 |  | DPM 4-20 |  | 1010 - Switched to operating mode |  | 7-CLICK |  |  |  | Input Channel 5 - J14 5, 6 | Lists |  |  |  |  | ALS | B45:H50 | C44:E44
| 37.5 |  | FLIGHT LIGHT |  |  |  | 1012 - Generator fuel tank level (%) | [5 empty] | Input Channel 6 - J14 3, 4 | Design |  |  |  |  | SFL | K5:Q10 | L4:N4
5-STEP 1-LOOP | 50 |  | HEVI-DUTY 57XXX SERIES |  |  |  | 1013 - Generator switch event | [5 empty] | Input Channel 7 - J14 1, 2 | [5 empty] | Beacon | K35:Q40 | L34:N34
5-STEP 2-LOOP | 70 |  | HEVI-DUTY 644 3A JUMPER |  |  |  | 1015 - New master CPU | [11 empty] | MALSR | K45:Q50 | L44:N44
5-STEP 3-LOOP |  |  | HEVI-DUTY 644 NEUT EXISTS |  |  |  | 1017 - New intensity and mode | [5 empty] | Output Channel 8 - J12 7, 8
5-STEP 4-LOOP |  |  | HONEYWELL |  |  |  | 1018 - New state | [5 empty] | Output Channel 9 - J12 5, 6
5-STEP SPARE |  |  | MANAIRCO |  |  |  | 1019 - I/O event | [5 empty] | Output Channel 10 - J12 3, 4
5-STEP CONTROL ONLY |  |  | ADB (SIEMENS) OIL-FILLED |  |  |  | 1020 - IPU power status | [5 empty] | Output Channel 11 - J12 1, 2
5-STEP COMBO BOX |  |  | ADB (SIEMENS) LC |  |  |  | 1021 - Hydro power status
ACE COMBO SPARE |  |  | ADB (SIEMENS) FERRO |  |  |  | 1022 - State changed | [5 empty] | Output Channel 12 - J11 7, 8
|  |  | ADB SIGNATURE FERRO |  |  |  | 1023 - Generator Running | [5 empty] | Output Channel 13 - J11 5, 6
3-STEP ACE II |  |  | ADB SIGNATURE THYRISTOR |  |  |  | 1024 - North Generator Transfer | [5 empty] | Output Channel 14 - J11 3, 4
3-STEP ACE II COMBO |  |  | UNKNOWN (GENERIC) |  |  |  | 1025 - South Generator Transfer | [5 empty] | Output Channel 15 - J11 1, 2
5-STEP ACE II |  |  | WESTINGHOUSE |  |  |  | 1026 - User acknowledged alarm
5-STEP ACE II COMBO | [6 empty] | 1027 - LAHSO Status | [5 empty] | Input Channel 16 - J13 15, 16
ACE II SPARE | [6 empty] | 1028 - L-854 Radio Control input | [5 empty] | Input Channel 17 - J13 13, 14
ACE II COMBO SPARE | [6 empty] | 1100 - Process started | [5 empty] | Input Channel 18 - J13 11, 12
[7 empty] | 1101 - Process stopped | [5 empty] | Input Channel 19 - J13 9, 10
PLC 1-STEP 1-LOOP | [6 empty] | 1102 - User logged on
PLC 1-STEP 2-LOOP | [6 empty] | 1103 - User logged off | [5 empty] | Input Channel 20 - J14 15, 16
PLC 1-STEP 3-LOOP | [6 empty] | 1200 - Transient link state change | [5 empty] | Input Channel 21 - J14 13, 14
PLC 1-STEP 4-LOOP | [6 empty] | 1300 - User test initiated | [5 empty] | Input Channel 22 - J14 11, 12
[7 empty] | 1320 - Failsafe initiating node shutdown | [5 empty] | Input Channel 23 - J14 9, 10
PLC 3-STEP 1-LOOP | [6 empty] | 1321 - Rebuilding a Hard Drive
PLC 3-STEP 2-LOOP | [6 empty] | 1322 - Rebuilding Hard Drive Completed | [5 empty] | Output Channel 24 - J12 15, 16
PLC 3-STEP 3-LOOP | [6 empty] | 1323 - Hard Drive was plugged in | [5 empty] | Output Channel 25 - J12 13, 14
PLC 3-STEP 4-LOOP | [6 empty] | 1324 - RAID Utility Application Started | [5 empty] | Output Channel 26 - J12 11, 12
[7 empty] | 1325 - RAID Utility Application Closed | [5 empty] | Output Channel 27 - J12 9, 10
PLC 5-STEP 1-LOOP | [6 empty] | 1326 - RAID Service Application Started
PLC 5-STEP 2-LOOP | [6 empty] | 1327 - RAID Service Application Stopped | [5 empty] | Output Channel 28 - J11 15, 16
PLC 5-STEP 3-LOOP | [6 empty] | 1361 - GO command issued to stopbar | [5 empty] | Output Channel 29 - J11 13, 14
PLC 5-STEP 4-LOOP | [6 empty] | 1362 - Proceed command issued to stopbar | [5 empty] | Output Channel 30 - J11 11, 12
[7 empty] | 1363 - Reset command issued to stopbar | [5 empty] | Output Channel 31 - J11 9, 10
1364 - Category change issued
1365 - Stopbar cycling
1366 - Segment out of service
1367 - New Segment State
1368 - New Master State
1369 - New Microwave Sensor State
1370 - New Global State
1371 - New Signal State
1372 - New Remote Replacement State
1420 - Debug info
1421 - Client has registered
1422 - Client has deregistered
1423 - Client being purged
1430 - ET200 debug info
1431 - ET200 client has registered
1432 - ET200 client has deregistered
1433 - ET200 client being purged
1440 - Debug info
1441 - Current temperature data
1460 - Insulation resistance measured
1490 - Current Fuel Level
1491 - Current Water Level
1492 - Current Fuel Temperature
1493 - Tank Empty Volume
1520 - Debug info
1521 - Client has registered
1522 - Client has deregistered
1523 - Client being purged
1571 - User Login
1572 - User Logout
1573 - Circuit Status
2300 - UPS communications error
2320 - Failsafe suspending process
2321 - No response from process
2323 - Hard Drive Critical at Startup
2324 - Hard Drive is Critical
3001 - Link failure
3002 - Link waited too long
3003 - UPS near low battery
3004 - UPS high battery
3005 - UPS low run-time left
3006 - UPS high AC output
3007 - UPS high ambient temperature
3008 - UPS heat-sink over temperature
3009 - UPS user-test mode
3010 - UPS undocumented warning
3011 - UPS cooling system malfunction
3012 - UPS battery malfunction
3013 - UPS inverter malfunction
3014 - UPS memory malfunction
3015 - UPS operation mode incorrect
3016 - UPS shutdown activated
3017 - Local mode
3018 - Lamps out warning
3019 - Warning
3022 - Flasher caution
3023 - Vault local control
3024 - ACE communication failure
3085 - Spare lamp in use
3086 - Unit caution
3087 - Thermal Sensor Warning
3200 - IPC link failure
3300 - UPS probe is missing
3301 - UPS near low battery condition
3302 - UPS high battery
3303 - UPS low runtime remaining
3304 - UPS high AC output
3305 - UPS high ambient temperature
3306 - UPS heat-sink over temperature
3307 - UPS check battery
3308 - UPS inverter malfunction
3309 - UPS memory malfunction
3310 - UPS transient temperature warning
3311 - UPS shutdown activated
3312 - UPS call service
3313 - UPS high AC input
3314 - UPS PFM temperature warning
3315 - UPS unknown warning
3316 - UPS site wiring warning
3317 - UPS fan warning
3318 - UPS no battery in UPS warning
3319 - UPS relay failure warning
3320 - Primary Hard Drive Failure
3321 - Mirrored Hard Drive Failure
3360 - VSP operation on SET 2
3361 - VSP operation on SET 3
3362 - BRITE remote unit failed
3363 - Stopbar inset lights failure
3364 - Stopbar left elevated lights failure
3365 - Stopbar right elevated lights failure
3366 - Stopbar intrusion sensor failure
3367 - Stopbar lead on group 1 failure
3368 - Stopbar lead on group 2 failure
3369 - Stopbar SET 2 sensor failure
3370 - Stopbar SET 3 sensor failure
3371 - VSP operation on SET 1
3372 - VSP operation on SET 4
3373 - Stopbar lead on group 3 failure
3374 - Stopbar SET 1 sensor failure
3375 - Stopbar SET 4 sensor failure
3376 - BRITE Fixture has an open lamp
3377 - Runway Guard bar warning
3378 - BRITE Segment warning
3379 - Burnt Lamp Detected on Channel A
3380 - Burnt Lamp Detected on Channel B
3381 - BRITE Segment warning
3382 - BRITE Remote Failed
3383 - BRITE System did not acknowledge TCH Command
3384 - Sensor Failed to Detect Object
3385 - PDX Lamp Burnt
3451 - Circuit resistance below warning limit
3530 - Approach low water level
3531 - Approach high water temp
3532 - Approach low lube oil PSI
3533 - Generator under voltage
3534 - Generator over voltage
3535 - Generator over frequency
3536 - Generator under frequency
3537 - Generator circuit breaker open
3538 - Generator circuit breaker closed
3539 - Gen room A/C air filter status
3540 - Lockout/Reset SW (Lockout/Reset)
3541 - Lockout/Reset SW (Off)
3542 - Lockout/Reset SW (Auto)
3543 - Lockout/Reset SW (Run)
3544 - Lockout/Auto SW (Lockout)
3545 - Lockout/Auto SW (Auto)
3546 - Auto load test SW (Auto)
3547 - Auto load test SW (Load test)
3548 - ATS Switch (ATS utility)
3549 - ATS Switch (ATS generator)
3550 - Bypass switch normal position
3551 - Bypass switch utility position
3552 - Bypass switch generator position
3553 - Utility Circuit breaker open
3554 - Utility Circuit breaker closed
3555 - Day tank fuel level 1/4
3556 - Day tank fuel level 1/2
3557 - Day tank fuel level 3/4
3558 - Day tank fuel level full
3559 - Kilowatt/Hr. meter
4011 - Circuit is in alarm
4012 - Failed to respond
4013 - Feedback does not match commanded state
4014 - Serial monitor board not responding
4015 - Inputs invalid
4016 - Open circuit
4017 - Over current
4018 - Lost primary power
4019 - Low VA
4020 - Incorrect current
4021 - Too many lamps out
4022 - CCR commanded on but current is not flowing in the loop
4023 - Current is flowing in the loop and the CCR is commanded off
4024 - A/D malfunction; Power reading
4025 - A/D malfunction; Lamps-out reading
4026 - CCR Input Alarm
4027 - In local mode
4028 - UPS power lost
4029 - UPS not responding
4030 - UPS low battery condition
4031 - UPS low AC output
4032 - UPS output overload
4033 - UPS bypassed
4034 - UPS summary mode active
4036 - I/O Event
4040 - Fail-safe enabled
4042 - Flasher fault
4043 - Not responding
4044 - Invalid feedback
4045 - Incorrect mode
4046 - Failed to respond
4048 - In local mode
4049 - Water in manhole too high
4050 - Commercial power failure
4051 - No generator available
4052 - North Vault AC Failed
4053 - South Vault AC Failed
4054 - North Vault Fire Alarm
4055 - South Vault Fire Alarm
4056 - Vault TVSS
4057 - Beacon in alarm
4058 - Generator off-line
4059 - Generator is unavailable
4060 - Utility power off-line
4061 - Utility power is unavailable
4062 - Protective shutdown
4063 - S7 Manager not responding
4064 - ET200 Manager not responding
4065 - Low fuel tank level
4066 - Overspeed
4067 - High engine jacket water temp
4068 - Low engine jacket water temp
4069 - Overcrank (failure to start)
4070 - Low oil pressure
4071 - Generator alarm
4075 - ACE failure
4076 - ACE Interface Server failure
4077 - ATS in Emergency
4085 - Door open
4086 - CCR Feedback does not match commanded state
4087 - General failure
4088 - Unit fault
4089 - Flash tube fault
4090 - Less than 3 lamps out
4091 - More than 3 lamps out
4092 - Loss of field power
4093 - LAHSO FAULT
4094 - LAHSO in local mode
4095 - Monitored lamp is out
4096 - PSC Manager not responding
4099 - Thermal Sensor Alarm
4300 - UPS has stopped responding
4301 - UPS low battery alarm
4302 - UPS low AC output
4303 - UPS output overload
4304 - UPS Running on battery power
4305 - UPS circuit breaker has shutdown
4320 - Unable to communicate with Dupli-Disk
4361 - Stop-bar communications path failure
4363 - BRITE PC link failure
4364 - BRITE master link failure
4365 - SMGCS system in failsafe
4366 - Stopbar inset lights failure
4367 - Stopbar left elevated lights failure
4368 - Stopbar right elevated lights failure
4369 - Stopbar intrusion detected
4370 - Stopbar lead on group 1 failure
4371 - Stopbar lead on group 2 failure
4372 - Stopbar in alarm
4373 - Stopbar lead on group 3 failure
4374 - Runway Guard Bar in alarm
4375 - BRITE Segment in alarm
4376 - BRITE Segment Alarm
4377 - Power Supply Failure
4378 - Loop Fault
4420 - S7 rack not responding
4430 - ET200 rack not responding
4431 - ET200 Moduled Removed
4440 - Temperature/Humidity measurement device not responding
4457 - Circuit resistance below alarm limit
4490 - High Fuel
4491 - Low Fuel
4492 - High Water
4493 - Fuel Theft
4494 - Fuel Leak
4495 - Auxiliary Contact
4496 - No Response from Auto/Stik
4520 - PSC rack not responding
4530 - Heat pump
4531 - Lift station status
4532 - Day tank low fuel level
4533 - Day tank fuel level empty
4534 - Fuel leak in tank or lines
4535 - Cold eng wtr jacket heater
4536 - UPS status
4537 - TVSS status
4538 - Util circuit breaker grnd fault
4539 - Gen circuit breaker grnd fault
4540 - Battery charger failure
4541 - D.C. critical control voltage fail
4542 - A.C. critical control voltage fail
4543 - Low water level
4544 - Engine running
Note on A1: Control Configuration
Note on C1: kW
Note on E1: CCROut
Note on G1: ManuModel
Note on I1: InMon
Note on K1: OutMon
Note on M1: Lamps
Note on O1: Desc
Note on Q1: Ctrl
Note on S1: Mon
Note on U1: SASProv
Note on W1: Vin
Note on Y1: InVolt
Note on AA1: ACE I/O
Note on AC1: Sheets tracked by logging.
Note on AH1: This space reserved for elements
Note on AJ1: Print for submittal sheets
Note on AL1: List of control tyes
Note on AM1: Range
Note on AN1: Header range

## Design (hidden)
Revision History |  |  |  | Action Items & Ideas
Rev # | Change Description | Author | Date | AI # | Description | Author | Date | Track To
A.0.0 | Added this tab to record changes. Added 3,5 Step 4,5 Loop Regulators to lists. Added fifth loop column. Added space for up to 100 regulators since DFW had 68 in one vault. Looked over the data validation on ccr index and removed clint sowers references. | wrigne | 2007-02-06 | 1 | Integrated the control methodolgy spreadsheet in to this one. | wrigne | 2007-03-29 | B.0.0
A.1.0 | Jimmy caught a bug. The logic still counted illegal characters against the character limit even though it removed them. I added code to prevent them from being counted. | wrigne | 2007-02-15 | 2 | Added the CCR SAT Test Sheets tab and functionality. | wrigne | 2007-04-24 | B.0.0
A.1.0 | Removed fifth loop column because Aap application can't handle it. | wrigne | 2007-02-15 | 3 | I'd like to replace al lthe equations on the CCR import tab with vba to reduce the total file size. This will be what the GET button will do on the CCR Import tab. | wrigne | 2007-04-26
B.0.0 | Actions Items: 1, 2, 4, 5, 6, 7 | wrigne | 2007-05-10 | 4 | I'd like to add all the touchscreen creations events on to the misc io tab, add ace IO and comm channels to the misc io tab. | wrigne | 2007-05-10 | B.0.0
B.1.0 | Action items: 8, 9 | wrigne | 2007-05-10 | 5 | I'd like to add user level tracking to this workbook as well. | wrigne | 2007-05-10 | B.0.0
B.2.0 | Actions 10, 11 | wrigne | 2007-05-11 | 6 | I'd like to replace all the equations on the control methodology tab with vba to reduce file size. | wrigne | 2007-05-10 | B.0.0
B.2.1 | Added the new CVM option for Seattle (CVM 4-20) | wrigne | 2007-06-01 | 7 | Add a button for printing a submittal package. | wrigne | 2007-05-10 | B.0.0
C.0.0 | Action 12, changed the 4-20 cvm to a 4-20 dpm. | wrigne | 2007-06-20 | 8 | Having equations under cells on the CCR index screws up the AAP import application in autocad. The application sees the equations as CCR data and attempts to draw stuff from them. I need to update the name formater code to add and remove the equations as needed. | wrigne | 2007-05-10 | B.1.0
|  |  |  | 9 | The misc io tabs new columns also screw with the Aap application. I need to move the ACE comm channel information to the end so the AAP application will ignore it. | wrigne | 2007-05-10 | B.1.0
|  |  |  | 10 | Added handling for user activity tracking to prevent error when previous value was not recorded by slection change. | nwright | 2007-05-11 | B.2.0
|  |  |  | 11 | Updated coding standard to use more global constants to minimize code maintenance. | nwright | 2007-05-11 | B.2.0
|  |  |  | 12 | Support fully FAA07110.65R | nhaines | 2007-06-04
|  |  |  | 13 | Support opposing directions | nhaines | 2007-06-04